## Slide 1
3rd Regional Symposium on Lifts & Escalators
LIFTS SUBJECT TO SEISMIC CONDITIONS
Seismic Categories of Lifts & Escalators – Safety Improvements
Goran Sekovski
ITI - Institute of technical inspection and safety engineering
25-26 September 2023, Skopje

## Slide 2: References
МКС EN 1998-1:2012 (Eurocode 8) – Design of structures for earthquake resistance - Part 1: General rules, seismic actions and rules for buildings;
MKC EN 1998-1/HA:2020 Eurocode 8 – Design of structures for earthquake resistance - Part 1: General rules, seismic actions and rules for buildings - National annex;
MKC EN 81-20:2020 Safety rules for the construction and installation of lifts - Lifts for the transport of persons and goods - Part 20: Passenger and goods passenger lifts;
МКС EN 81-77:2022 – Safety rules for the construction and installations of lifts - Particular applications for passenger and goods passenger lifts - Part 77: Lifts subject to seismic conditions;
МКС EN 115-1:2017 - Safety of escalators and moving walks - Part 1: Construction and installation;
МКТС CEN/TS 115-4:2021 - Safety of escalators and moving walks - Part 4: Interpretations related to EN 115 family of standards;
GUIDELINES – Lifts, escalators and moving walks under seismic conditions, ed. 2021, European Lift Association - ESMO Working group.

## Slide 3
Lifts

## Slide 4: Determination of the design acceleration
The annotations are according to those in МКС EN 1998-1:2012 Еurocode 8:
ad – design acceleration (m/s2);
g – free fall (gravity) acceleration (m/s2);
Sa – seismic coefficient applicable for nonstructural elements;
γa – importance factor of the element (it is taken as unity (1), while for security lifts, the value is increased in compliance with Eurocode 8. Security lifts are those installed in hospitals or those for emergency situations or evacuation – the factor presented below has been selected according to that for structural elements);
qa – factor of element behaviour (it is taken as 2);
α – ratio between design ground acceleration for soil type A (ag) according to Eurocode 8 and ground acceleration (g);
S – soil factor according to Eurocode 8;
Ta – fundamental period of vibration of a nonstructural element (Ta = 0 if the lift does not affect the fundamental period of vibration of the building. For the remaining cases, it is computed and is greater than 0)(s);
T1 – fundamental period of vibration of the building in a specified direction (s);
z – height of the nonstructural element above the level of the seismic force effect (m);
H – height of the building measured from the top of the foundation, considering the ground as level 0 (m); Table 1. Seismic categories of lifts (Annex A to МКС EN 81-77:2019.

## Slide 5: Seismic categories of lifts (Annex A to МКС EN 81-77:2022)
Design acceleration (m/s2) | Seismic category of lifts | Note
1 < ad ≤ 2,5 | 1 | Minor correction actions required
2,5 < ad ≤ 4 | 2 | Medium correction actions required
ad> 4 | 3 | Substantial corrective actions required

## Slide 6: Seismic zoning of North Macedonia
TNCR = 475 years - reference return period of the seismic action for the no-collapse requirement or equivalently PNCR = 50 years - reference probability of exceedance

## Slide 7: Seismic categories of lifts in North Macedonia
Seismic zone Z-5 (ad = 0,30 g) |  |  |  |  |  | 
α = | 0,30 | S | Sa | ad |  | 
 | Type of soil |  |  | γ (II) | γ (III) | γ (IV)
 |  |  |  | 1,0 | 1,2 | 1,4
 | A | 1,00 | 0,7500 | 3,6788 | 4,4145 | 5,1503
 | B | 1,20 | 0,9000 | 4,4145 | 5,2974 | 6,1803
 | C | 1,15 | 0,8625 | 4,2306 | 5,0767 | 5,9228
Seismic zone Z-4 (ad = 0,25 g) |  |  |  |  |  | 
α = | 0,25 | S | Sa | ad |  | 
 | Type of soil |  |  | γ (II) | γ (III) | γ (IV)
 |  |  |  | 1,0 | 1,2 | 1,4
 | A | 1,00 | 0,6250 | 3,0656 | 3,6788 | 4,2919
 | B | 1,20 | 0,7500 | 3,6788 | 4,4145 | 5,1503
 | C | 1,15 | 0,7188 | 3,5255 | 4,2306 | 4,9357
Seismic zone Z-3 (ad = 0,20 g) |  |  |  |  |  | 
α = | 0,20 | S | Sa | ad |  | 
 | Type of soil |  |  | γ (II) | γ (III) | γ (IV)
 |  |  |  | 1,0 | 1,2 | 1,4
 | A | 1,00 | 0,5000 | 2,4525 | 2,943 | 3,4335
 | B | 1,20 | 0,6000 | 2,9430 | 3,5316 | 4,1202
 | C | 1,15 | 0,5750 | 2,8204 | 3,3845 | 3,9485
Seismic zone Z-2 (ad = 0,15 g) |  |  |  |  |  | 
α = | 0,15 | S | Sa | ad |  | 
 | Type of soil |  |  | γ (II) | γ (III) | γ (IV)
 |  |  |  | 1,0 | 1,2 | 1,4
 | A | 1 | 0,3750 | 1,8394 | 2,2073 | 2,5751
 | B | 1,20 | 0,4500 | 2,2073 | 2,6487 | 3,0902
 | C | 1,15 | 0,4313 | 2,1153 | 2,5383 | 2,9614
Seismic zone Z-1 (ad = 0,10 g) |  |  |  |  |  | 
α = | 0,10 | S | Sa | ad |  | 
 | Type of soil |  |  | γ (II) | γ (III) | γ (IV)
 |  |  |  | 1,0 | 1,2 | 1,4
 | A | 1 | 0,2500 | 1,2263 | 1,4715 | 1,7168
 | B | 1,20 | 0,3000 | 1,4715 | 1,7658 | 2,0601
 | C | 1,15 | 0,2875 | 1,4102 | 1,6922 | 1,9743
Seismic category of lifts | 
0 | 
1 | 
2 | 
3 | 
Debar, Struga, Ohrid, Pehchevo, Berovo and Valandovo
Skopje, Strumica, Mavrovo and Delchevo
Gevgelija, Kochani, Radovish, Kumanovo, Tetovo, Gostivar, Kichevo and Resen
Kriva Palanka, Shtip, Veles, Negotino, Kavadarci and Bitola
Prilep
Definition of seismic categories of lifts according to
МКС EN 81-77:2022 standard

## Slide 8: Additional safety measures for new lifts in seismic conditions
In addition to the computation for the guide rails proposed in Annex D to the MKS EN 81-77:2022 standard for lifts in seismic conditions, the standard also anticipates a series of other measures for improvement of safety of lifts in seismic zones for categories 1, 2 and 3 prescribed by the same standard.
For lifts of seismic category 0, it is not necessary to take any additional corrective measures whereat it is considered that the essential safety requirements pertaining to MKC EN 81-20:2020 and MKC EN 81-50:2020 are sufficient enough.

## Slide 9: Additional measures for lifts belonging to seismic categories 1, 2 and 3
Additional requirements for lifts of seismic categories 1, 2 and 3 are anticipated for: the lift well (protection of snag points), the machine room, the counterweight guide rails or the balance guide rails (specific calculation), the bearing and compensation devices, the guide rails (car and counterweight retaining device), the traction pulley (retainer) etc. (see standard МКС EN 81-77:2022.
Where buildings are designed with expansion joints subdividing the structure into dynamically independent units, all the lift machinery including the landing entrances and the well of the lift shall be located on the same side of an expansion joint

## Slide 10: Additional measures for lifts belonging to seismic categories 2 and 3
In addition to the measures taken for categories 1, 2 and 3 (general requirement for lifts subject of seismic conditions) to be satisfied the following measures should be taken for lifts categorized into seismic categories 2 and 3:
The car, i.e., the frame of the car should be provided with a retaining device that will prevent displacement of the car from the guide rails and uncontrolled motion beyond the defined direction.
The lending doors should be prevented from opening as described in provisions 5.3.9. for the general case and in special cases in item 5.3.9.1. of the standard Locking and unlocking of the lending doors and car doors in emergency cases should be compliant with the MKC EN 81-20:2020 standard.
For the purpose of avoiding the possibility for people to be stuck in a car between two storeys, there should be a device that will move the car to the first upper or lower level.

## Slide 11: Additional measures only for lifts belonging to seismic category 3
In addition to the previously stated devices for seismic category 1 and those for categories 2 and 3, electrical lifts with a counterweight categorized into seismic zone 3 should be equipped with a seismic detection device and additionally, by way of negotiations and consent given by the owner, but not obligatorily, a system for detection of primary waves. Considering that primary seismic waves are the fastest in their propagation, this system is very efficient and has been increasingly applied since it safely brings the car to a stop prior to the arrival of the secondary and the most destructive surface waves.

## Slide 12: ELA Guidelines
Protective measures described in EN81-77 are based on the required measures in each of the lift categories.

## Slide 13
Escalators and moving walks

## Slide 14: Annex M (normative) of MKC EN 115-1: Escalators and moving walks subject to seismic conditions
Structural requirements
Supports
The support conditions of the escalators and moving walks in combination with the building shall be secured so that the escalators and moving walks under seismic conditions are not subjected to constraint. One support shall be designed as fixed support the other supports shall be designed as movable in horizontal direction. The supporting conditions shall be simple statically determined.
Escalators and moving walks shall be retained on the supports in vertical direction by adequate measures so that they cannot be displaced from the supports under seismic conditions.
Arrangement
The length and the movability of the escalators and moving walks shall be chosen in accordance with the building movement between two storeys of the building. The supports shall be designed so that they overlap the building interface. For the determination of the overlap the theoretical maximum “storey drift” of the building shall be used.
Mechanical safety devices for escalators and moving walks
If the design of the escalators and moving walks in combination with the building does not ensure that the escalator or moving walk remains in safe position on the supports, then an additional mechanical safety device shall be applied, so that the escalator and moving walk cannot fall off the supports.

## Slide 15: Annex M (normative) of MKC EN 115-1: Escalators and moving walks subject to seismic conditions
Design requirements
Truss
Based on the requirements of EN 1998-1:2004 the design of the truss for the escalators and moving walks shall be sufficiently executed for the ambient seismic condition. The structural design shall provide a dissipation capacity to withstand a design-relevant earthquake of the region where it is located
Mass for the truss of escalators and moving walks
For design calculations of escalators and moving walks the forces shall be determined with the agreed ground acceleration (agR).
For the determination of horizontal and vertical forces on escalators and moving walks the dead weight plus the step load, given in Table M.1, shall be used.
The step load is determined by the maximum capacity of the escalator according to H.1 with an average weight of 75 kg per person.
Nominal speed m/s | Step width m | Step depth m | Max capacity Pers./h | Max capacity Pers./s | Travel time /step s | Person/ step | Person weight kg | Step load kg/step
0,50 | 1,00 | 0,40 | 6 000 | 1,67 | 0,80 | 1,33 | 75 | 100
Table M.1 — Step load determination
With a factor ψ of 0,6 (taken from EN 1990:2013, Table A.1, category C/D) this leads to a seismic step load QSE of 60 kg per step.

## Slide 16: Annex M (normative) of MKC EN 115-1: Escalators and moving walks subject to seismic conditions
Design requirements
Condition of loading and deformation during a seismic event
For calculation the seismic condition shall be classified as an exceptional load case. In in areas of regular seismic activity the load case shall be classified as standard variable load.
Superposition rules and safety factors shall be chosen in accordance with EN 1990:200215), EN 1993-1-1:2005 and EN 1998-1:2004.
Plastic deformation is permitted as long as it does not influence the structural integrity of the truss and supports. The structural integrity of the truss with supports and the safe operability (function) of the escalator or moving walk shall be inspected by experts after the seismic event before the escalator or moving walk can be put back to operation.
The importance factor γI shall be chosen as 0,85.
Friction for supports does not need to be considered in support reaction calculations.
Calculation procedure according to EN 1998-1:2004
The calculation procedure shall be undertaken in accordance with Figure M.1.

## Slide 17: Annex M (normative) of MKC EN 115-1: Escalators and moving walks subject to seismic conditions
Figure M.1 — Calculation procedure according to EN 1998-1:2004

## Slide 18: ELA Guidelines
This guideline is referring to the interpretation N148 in CEN/TS115-4 with the following diagram
EN115-1 speciﬁes two seismic categories for escalators and moving walks.

## Slide 19: ELA Guidelines

## Slide 20
THANK YOU